AGS ROLL GROOVE SPECIFICATIONS

For Carbon Steel Pipe And S.S Pipe

--Organized By WELPING & GruvMaster

| - Actual Pipe Outside Diameter mm | - Dimensions - millimeters (mm) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | - Pipe Outside Diameter |  | - Gasket Seat “A” |  |  | - Groove - Width - "B" | - Groove Diameter “C” |  | - Norminal Wall Thickness for Grooving "T" |  | - Max. Allow. Flare Dia. “F” |
|  | - Max. | - Min. | - Basic | - Max. | - Min. |  | - Max. | - Min. | - Carbon Steel | - S.S Steel Sch.10S |  |
| - 355.6mm | - 358.0 | - 354.8 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 342.9 | - 341.8 | - 5.6–19.1 | - 4.8 | - 361.4 |
| - 377.0mm | - 379.4 | - 376.2 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 364.3 | - 363.2 | - 5.5–19.1 | – | - 382.8 |
| - 406.4mm | - 408.8 | - 405.6 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 393.7 | - 392.6 | - 6.4–19.1 | - 4.8 | - 412.2 |
| - 426.0mm | - 428.4 | - 425.2 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 413.3 | - 412.2 | - 6.5–19.1 | – | - 431.8 |
| - 457.2mm | - 459.6 | - 456.4 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 444.5 | - 443.4 | - 6.4–19.1 | - 4.8 | - 463.0 |
| - 480.0mm | - 482.4 | - 479.2 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 467.3 | - 466.2 | - 6.5–19.1 | – | - 485.9 |
| - 508.0mm | - 510.4 | - 507.2 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 495.3 | - 494.2 | - 6.4–19.1 | - 5.5 | - 513.8 |
| - 530.0mm | - 532.4 | - 529.2 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 517.3 | - 516.2 | - 6.5–19.1 | – | - 535.7 |
| - 558.8mm | - 561.2 | - 558.0 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 546.1 | - 545.0 | - 6.4–19.1 | - 5.5 | - 564.6 |
| - 609.6mm | - 612.0 | - 608.8 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 596.9 | - 595.8 | - 6.4–19.1 | - 5.5 | - 615.4 |
| - 630.0mm | - 632.4 | - 629.2 | - 38.1 | - 38.89 | - 36.5 | - 11.6 | - 617.3 | - 616.2 | - 6.5–19.1 | - – | - 635.8 |
| - 660.4mm | - 662.0 | - 658.8 | - 44.5 | - 45.29 | - 42.9 | - 13.6 | - 645.9 | - 644.4 | - 8.0–19.1 | - – | - 668.0 |
| - 711.2mm | - 712.8 | - 709.6 | - 44.5 | - 45.29 | - 42.9 | - 13.6 | - 696.7 | - 695.2 | - 8.0–19.1 | - – | - 718.8 |
| - 720.0mm | - 721.6 | - 718.4 | - 44.5 | - 45.29 | - 42.9 | - 13.6 | - 705.5 | - 704.0 | - 8.0–19.1 | - – | - 727.6 |
| - 762.0mm | - 763.6 | - 760.4 | - 44.5 | - 45.29 | - 42.9 | - 13.6 | - 747.5 | - 746.0 | - 8.0–19.1 | - – | - 769.6 |
| - 812.8mm | - 814.4 | - 811.2 | - 44.5 | - 45.29 | - 42.9 | - 13.6 | - 798.3 | - 796.8 | - 8.0–19.1 | - – | - 820.4 |
| - 820.0mm | - 821.6 | - 818.4 | - 44.5 | - 45.29 | - 42.9 | - 13.6 | - 805.5 | - 804.0 | - 8.0–19.1 | - – | - 827.6 |
| - 863.6mm | - 865.2 | - 862.0 | - 44.5 | - 45.29 | - 42.9 | - 13.6 | - 849.1 | - 847.6 | - 8.0–19.1 | - – | - 871.2 |
| - 914.4mm | - 916.0 | - 912.8 | - 44.5 | - 45.29 | - 42.9 | - 13.6 | - 899.9 | - 898.4 | - 8.0–19.1 | - – | - 922.0 |
| - 920.0mm | - 921.6 | - 918.4 | - 44.5 | - 45.29 | - 42.9 | - 13.6 | - 905.5 | - 904.0 | - 8.0–19.1 | - – | - 927.6 |
| - 965.0mm | - 966.6 | - 963.4 | - 44.5 | - 45.29 | - 42.9 | - 13.6 | - 950.7 | - 949.2 | - 8.0–19.1 | - – | - 972.8 |
| - 1016.0mm | - 1017.6 | - 1014.4 | - 50.8 | - 51.59 | - 49.2 | - 14.3 | - 1000.1 | - 998.6 | - 8.0–19.1 | - – | - 1023.6 |
| - 1066.8mm | - 1068.4 | - 1065.2 | - 50.8 | - 51.59 | - 49.2 | - 14.3 | - 1050.9 | - 1049.4 | - 8.0–19.1 | - – | - 1074.4 |
| - 1117.6mm | - 1119.2 | - 1116.0 | - 50.8 | - 51.59 | - 49.2 | - 14.3 | - 1101.7 | - 1100.2 | - 8.0–19.1 | - – | - 1125.2 |
| - 1168.4mm | - 1170.0 | - 1166.8 | - 50.8 | - 51.59 | - 49.2 | - 14.3 | - 1152.5 | - 1151.0 | - 8.0–19.1 | - – | - 1176.0 |
| - 1219.2mm | - 1220.8 | - 1217.6 | - 50.8 | - 51.59 | - 49.2 | - 14.3 | - 1203.3 | - 1201.8 | - 8.0–19.1 | - – | - 1226.8 |
| - 1270.0mm | - 1271.6 | - 1268.4 | - 50.8 | - 51.59 | - 49.2 | - 14.3 | - 1254.1 | - 1252.6 | - 8.0–19.1 | - – | - 1277.6 |
| - 1371.6mm | - 1373.2 | - 1370.0 | - 63.5 | - 64.29 | - 61.9 | - 14.3 | - 1357.1 | - 1355.6 | - 9.5–19.1 | - – | - 1379.2 |
| - 1422.4mm | - 1424.0 | - 1420.8 | - 63.5 | - 64.29 | - 61.9 | - 14.3 | - 1407.9 | - 1406.4 | - 9.5–19.1 | - – | - 1430.0 |
| - 1473.2mm | - 1474.8 | - 1471.6 | - 63.5 | - 64.29 | - 61.9 | - 14.3 | - 1458.7 | - 1457.2 | - 9.5–19.1 | - – | - 1480.8 |

AGS ROLL GROOVE SPECIFICATIONS

For Carbon Steel Pipe And S.S Pipe

--Organized By WELPING & GruvMaster

| - Actual Pipe Outside Diameter mm | - Dimensions - millimeters (mm) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | - Pipe Outside Diameter |  | - Gasket Seat “A” |  |  | - Groove Width “B” | - Groove Diameter “C” |  | - Norminal Wall Thickness for Grooving "T" |  | - Max. Allow. Flare Dia. “F” |
|  | - Max. | - Min. | - Basic | - Max. | - Min. |  | - Max. | - Min. | - Carbon Steel | - S.S Steel Sch.10S |  |
| - 1524.0mm | - 1525.6 | - 1522.4 | - 63.5 | - 64.29 | - 61.9 | - 14.3 | - 1509.5 | - 1508.0 | - 9.5–19.1 | - – | - 1531.6 |
| - 1574.8mm | - 1576.4 | - 1573.2 | - 63.5 | - 64.29 | - 61.9 | - 14.3 | - 1560.3 | - 1558.8 | - 9.5–19.1 | - – | - 1582.4 |
| - 1625.6mm | - 1627.2 | - 1624.0 | - 63.5 | - 64.29 | - 61.9 | 14.3 | - 1611.1 | - 1609.6 | - 12.7–19.1 | - – | - 1633.2 |
| - 1676.4mm | - 1678.0 | - 1674.8 | - 63.5 | - 64.29 | - 61.9 | 14.3 | - 1661.9 | - 1660.4 | - 12.7–19.1 | - – | - 1684.0 |
| - 1727.2mm | - 1728.8 | - 1725.6 | - 63.5 | - 64.29 | - 61.9 | 14.3 | - 1712.7 | - 1711.2 | - 12.7–19.1 | - – | - 1734.8 |
| - 1828.8mm | - 1830.4 | - 1827.2 | - 63.5 | - 64.29 | - 61.9 | 14.3 | - 1814.3 | - 1812.8 | - 12.7–19.1 | - – | - 1836.4 |
| - 1981.2mm | - 1982.8 | - 1979.6 | - 63.5 | - 64.29 | - 61.9 | 14.3 | - 1966.7 | - 1965.2 | - 12.7–19.1 | - – | - 1990.3 |